MM200 Guideform Specifications

October 2008

NOTE TO SPECIFIER:

For more information on this product visit the GE Multilin Web Site for a product brochure and instruction manual at

http://www.gedigitalenergy.com/multilin/brochure/mm200.htm

http://www.gedigitalenergy.com/multilin/manuals/mm200.htm

The motor management relay shall provide primary protection and management to low voltage motors rated 690 Volts and below.   The relay shall be equipped with the following protection functions.

Motor Thermal Overload Model (49)

  - The Thermal Model shall consist of the following:

  - Include 15 standard overload curves

  - Hot/cold biasing that accounts for normal temperature rise.

  - Cooling rate that accounts for heat dissipation

  - Thermal protection reset that controls recovery from thermal trips and lockouts.

The relay shall detect ground faults or earth leakage currents as low as 0.50 A using a 50:0.025 Ground CT.

Use phase current heating to calculate motor thermal capacity during starting and running states

Settable motor stopped and motor running cooling time constants

Ground Instantaneous overcurrent elements (50G)

Unbalance / single phase biasing (46)

Load-loss (undercurrent) (37)

Ground time overcurrent (51G)

Locked/stalled rotor, mechanical jam (51R)

Motor stall protection

The relay shall be equipped with an acceleration timer

The relay shall be equipped with a load increase alarm

The relay shall have a thermistor input.

The relays shall have internal Current Transformers (C.T.’s) rated and 1A/5A and shall be suitable for direct connection up to 5A FLA.

The relay power supply shall be rated at 24VDC or an AC power supply rated at 60 – 300VAC

The relays shall be capable of operating with 50Hz and 60 Hz systems

The relay shall have programmed starter logic and shall support the following starter types.  Full Voltage Non-Reversing (FVNR), Full Voltage Reversing (FVR), Two Speed.

  - Inputs and Outputs shall be automatically assigned based on the starter type.

The relay shall be capable of being DIN rail mounted.

- Digital Inputs

  - The relay shall have two (2) Form A and one (1) Form C outputs.

  - The relay shall have seven (7) digital inputs rated at 24VDC.

  - Or

  - The relay shall have two (2) Form A and one (1) Form C outputs.

  - The relay shall have six (6) digital inputs rated at 65 to 300 VAC.

- The relay shall be suitable to operate in temperatures from –20 degrees Celsius to +60 degrees Celsius with up to 90% non-condensing humidity.

The relay shall provide complete monitoring and metering functions. These shall include:

Current: RMS Values of per Phase, Average Current, Ground Current, Motor Load, Current Unbalance, Thermal Capacity

The relay shall provide the following information:

  - Total number of trips

  - Overload trips

  - Mechanical jam trips

  - Undercurrent trips

  - Current Unbalance trips

  - Ground fault trips

  - Motor acceleration trips

The relay shall capture the number of motor starts and motor running hours.

The following learned data shall be provided:

  - Learned acceleration time

  - Learned starting current

  - Learned starting capacity

  - Learned average motor load

User interfaces shall include:

A control panel shall be available with the relay

The control panel shall include the following:

  - Start A, Start B and Stop pushbuttons

  - Auto/Manual/Reset pushbuttons

  - LED indicators:

    - Running, Stopped, Tripped, Alarm, Comms OK, Auto, Manual

    - Motor load 50%, 80%, 100%

    - User Programmable designated as, User 1 and User 2.

    - LED color indication shall change based on condition

The relay shall be capable of being set by Windows-based, Easy to use, Setup graphical terminal interface

Communications

The relay shall have one RS485 port. The communications protocol shall be Modbus RTU.  Baud rate for RS485 shall be from 9600 to 115200 baud.

An optional terminal port shall be provided to allow DeviceNet (125, 250 or 500 kps) or Profibus connectivity to Local DeviceNet or Profibus Networks.

The relay shall be capable of communicating through all communication protocols simultaneously and without the use of protocol converters.

The relay shall be capable of being programmed by a Windows-based, Easy to use, Setup graphical terminal interface

Approvals

The relay shall be manufactured under an ISO9001 registered program

The relay shall be cUL Listed

The relay shall conform to EN 60255-26 (EN 50263), EN 5502 / CISPR22 / EN61000-6-2

The relay shall conform to UL 508 / UL 1053 and C22.2.14.05 (CSA)